## Slide 1: ‘Calm, Cool & Collected’
Selecting the right sensor for Hazardous Environments
Sponsored by:
Everight Position, POSTIAL and Positek

## Slide 2: Overview
What is a ‘Hazardous Location (HazLoc)’
How are devices made to operate in a Hazardous Location
  Intrinsically Safe
  Explosion Proof
Sensors developed for HazLoc
Q+A
Disclaimer: Final decisions on products in a hazardous location must be made by a Safety Engineer who has complete knowledge of the entire location.

## Slide 3: Designing Systems In a ‘Hazardous Location’
Dangerous?
Confusing?
Overwhelming?
Humbling?

## Slide 4: What is a ‘Hazardous Location’
“Hazardous areas exist where a potentially explosive mix of air and flammable gasses or air and dust or air, dust and gasses may occur.”
Chemistry 101
  To cause a reaction you need:
    Fuel
    Oxygen
    Ignition Source
Image credit

## Slide 5: Potential Ignition Sources
Open flames
  A lit cigarette to welding sparks
Lightning strikes
Impact sparks
  ie. Hammer blow on a rusty surface vs hammer blow on a flint stone
Mechanically generated friction sparks
Electrical sparks
Electrostatic discharge
High surface temperature

## Slide 6: HazLoc’s Are Common
Could be a:
  Chemical refinery
  Fuel station
  Paint booth
  Mining
    Coal dust
  Agriculture
    Grain mills, sugar refineries, silos
  Printing industries, paper and textiles
  Sewage treatment plants
  And the list goes on…

## Slide 7: HazLoc
Zone 0
  Explosive atmosphere is present continuously for long periods of time or will frequently occur.
Zone 1
  Explosive atmosphere is likely to occur occasionally in normal operation. It may exist because of repair, maintenance operations, or leakage.
Zone 2
  Explosive atmosphere is not likely to occur in normal operation but, if it does occur, will persist for a short period only.
  These areas only become hazardous in case of an accident or some unusual operating condition.
Image credit: heatingandprocess.com

## Slide 8: Devices – Intrinsically Safe
Can’t remove the fuel, so engineers remove the ignition source
Intrinsically Safe (IS)
  An IS device is “incapable of releasing sufficient electrical or thermal energy under normal or abnormal conditions to cause ignition of a specific hazardous atmospheric mixture in its most easily ignited concentration”
  Accomplished in IS devices by limiting the amount of power to be below the level that will ignite the atmosphere

## Slide 9: Devices – Intrinsically Safe
Most commonly an IS barrier is wired in series with the device
The barrier is located in a ‘safe zone’ outside of the explosive atmosphere
Barriers typically use
  Zener Diodes to limit voltage
  Resistors to limit current
  Fuse
Temperature must still be considered
Omega link

## Slide 10: Devices – Non-Sparking
Design prevents sparking or excess temperatures under normal circumstances
Designed for least stringent environments
Explosive atmosphere is not usually present

## Slide 11: Devices – Flame-Proof
An explosion occurring inside encoder will not propagate to environment

## Slide 12: Devices – Explosion Proof
Can’t remove the fuel, so engineers contain the ignition
‘Explosion Proof’
  If an explosive atmosphere penetrates into an enclosure and a trigger is produced; the explosion occurs, but it remains confined within the enclosure
    Does not allow the spread of flame to the surrounding atmosphere
    External temperature of the housing will not get hot enough to ignite vapors in the area
  Enclosures must be constructed with
    Mechanical strength such as to contain the overpressure caused by the explosion
    Allow the escape of flue gases (flame path)
      Allows the gases to exit the enclosure and to cool down during the passage, so that they are no longer able to trigger the outside atmosphere
https://www.cortemgroup.com/en/about-ex/technical-articles/evolution-ex-proof-flame-path

## Slide 13: Devices – Explosion Proof
Since Ex Proof devices are largely mechanical changes, communicating with them is similar to industrial devices
No additional barrier as for IS devices
Analogous devices for ‘safe’ environments are often available
  Reduce cost and overall system complexity
Image Credit: National Electrical Code Handbook, 2017 Edition

## Slide 14: Regulatory
CSA
UL
ATEX
IECEx
CCC

## Slide 15: Labeling
North America
Europe

## Slide 16: Labeling
Ability to use ATEX in N. America and use UL/CSA in Europe is often a case-by-case decision for the safety engineer for the project
More on Class+Div VS. Zone https://www.ul.com/services/ul-and-c-ul-hazardous-areas-certification-north-america

## Slide 17: Labeling – Class+Div VS Zone

## Slide 18: Sensors
Broad variety of sensors on the market for use in hazardous environments
  Rotary
  Tilt
  Linear
  Temperature
  Pressure
  etc

## Slide 19: POSITAL
Founded in Germany in 1918
Growing global presence in last 20 year
Focus is on elimination of active ignition source

## Slide 20: POSITAL - Products
Rotary encoders and inclinometers
Large Variety of the Ex-Products
Universal Compact Mechanical Designs
Easy Application Installation
Products with Global View of the Regional Ex-Certification

## Slide 21: POSITAL - Approach
Non Sparking Type “nA”
Design prevents sparking or excess temperatures
  Seals
  Glands
  Produced by only trained workers
Dedicated for:
Zone 2 & 22
Div. 2 Class I
Certification:
Manufacture Self-declaration ATEX
Profinet Encoder for Div.2 Class I
Future:
3rd party certification for ATEX/IECEX*
Extend UL/CSA for Div. 2 class I/II*
CCC – China*
*Certification project in progress

## Slide 22: POSITAL - Approach
Flameproof Enclosure Type “d”
An explosion occurring inside encoder will not propagate to environment
  Thicker housings
  Flame paths
Certification:
ATEX & IECEx
Future:
CCC – China*
Dedicated for:
Zone 1 & 21
Underground Mining

## Slide 23: POSITAL - Approach
Only MEMS based ATEX inclinometer in the world
Encapsulation type “m”
  Keeps the potentially explosive atmosphere away from the source of ignition
Certification:
ATEX & IECEx
Future:
CCC – China*
Dedicated for:
Zone 1 & 21
Underground Mining
*Certification project in progress

## Slide 24
ATEX/IECEx/ULCertification Available
Available with Ethernet, Digital, Analog and Incremental Interfaces
No Battery Backup
Removable Connection Cap Or Cable Exit
Group I And Group II Certification
Zone 1 (Gas), 21 (Dust) And 2 (Gas), 22 (Dust)
High Resolution Up To 16 Bit And Revolution 14 Bit
Incremental Encoders Programmable
Available Also in V4A Stainless Steel
Project Customization Possible
Posital – Product Highlights

## Slide 25: Positek
Founded in the UK in 1992
Part of VariOhm/Discoverie
Focus of HazLoc products is on Intrinsic Safety

## Slide 26: Positek - Products
Short stroke linear (< 1 meter) are dominant products
  Also rotary encoders and inclinometers
Large Variety of the Ex-Products
Short lead times
  4 weeks standard
  1 week expedited
Safe Area
Hazardous Area

## Slide 27: Positek – Intrinsically Safe
All Positek HazLoc products rely on the use of:
  Galvanically isolated amplifier barrier
    Located in safe area
    Limits electrical and thermal energy into the hazardous area
  0.5->4.5V output ratiometric circuit
  Barrier can output voltage or current signal
  Optional 5 wire installation
    Negate the effects of loss over the wires and thermal effects
    Up to 1,000 m between barrier and sensor

## Slide 28: Positek – Environment Options
ATEX/IECEx approved to:
  Ex II 1G
  Ex ia IIC T4 GA (Ta = -40°C to +80°C)
  Group II Category 1 G
CSA approved to:
  Class I, Zone 0
  Ex ia IIC T4 (Ta = -40°C to +80°C)
  AEx ia IIC T4 (Ta = -40°C to +80°C)

## Slide 29: Positek – Product Series
Linear Position Sensors
Applications :
Paper manufacturing
Power turbines
Hydraulics
Offshore rigs
Rotary Position Sensors
Applications :
Automotive
Industrial control
Valve control
Tilt Position Sensors
Applications :
- Industrial machinery
- Vehicles, planes & marine

## Slide 30: Positek - Linear
_100 Linear-Cylinder Position Sensor
_101/111 Stand Alone Linear Position Sensor
_106 Internally Mounted Cylinder Sensor
_103/133 Linear Sensor
_112 Gauge Head Linear Position Sensor
_116 Internally Mounted Cylinder Sensor
_117 Slim Line linear Position Sensor
_118/138 Slim Line Linear Sensor
_130 Long Stroke In- Cylinder Sensor

## Slide 31: Thank you
Thank you to
  Wojtek Pajak of POSITAL
  Mark Spreadbury of Positek
  You for joining us
For more info
  Jarrod Orszulak
  Everight Position
    jarrod@evrtp.com
    www.evrtp.com
    856 727 9500